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	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:


	Vendor kindly asks to receive following information from ECPI contractor necessary to properly analyze and design the installation elements for installation of the containers on the platform:
BLPH:
1. Please provide floor/deck material of the rig the containers will be resting on.
1. Please provide plate thickness.
1. Is it suitable to bolt the containers to the deck and is there access underneath the deck for securing bolts, or will hollo-bolts be required?
1. Can the base plates be welded to the deck to secure the containers?








	2. Response

	

	Reference documents / Aconex unique numbers
Vendor to consider following replies :

1) BLPH floor/deck plates are in steel material
2) Plate thickness below BESS package is 8mm, but it will be increase in correspondence of BESS package support points where necessary.


3) Access underneath deck for securing bolts is not available. If container supports are as following:
[image: ]
Bolted connection (1,2,3) will be as per following figure:

[image: ]


4) Can the base plates be welded to the deck to secure the containers?
In case of supports as per following figure:
[image: ]
Preferred solution is to bolt the base plate to the main flooring plate.

In case of beam supports, preferred solution is as per following figure:
[image: ]


CLOSE OUT

STATRON-INN-BPH-MAN-00006
Container Installation Manual

TQ answered via above document
Subject closed 





This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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