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TECHNICAL QUERY
Hollandse Kust Noord

	Employers query to
	@@
	No:
	@@
	Rev:
	A

	Subject
	@@  
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	No. TD :
	123A90-PML-PM-DR-00001
	Rev:
	00



	Originating Party
	RosettiMarino

	Subject
	Escape Route – change from primary to secondary in a limited area

	Author
	C. Caracciolo
	TQ Aconex unique number:  ROSMA-INN-BPH-DEV-00006

	Interface TQ - from
	P. Van Rossum
	TQ interface source Aconex unique number:  



	Type
	Query
	
	Interface
	

	
	Deviation
	x
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	x
	Procurement
	
	Construction
	

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	
	Urgent reply 5 days
	
	Routine reply 10 days
	x

	Close-out date
	
	

	Closed-out by
	
	TD status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	3D model and Escape route, fire fighting, life saving equipment and safety equipment layouts drawings, doc. N. 
123A90-DDL-SAF-DL-30025 rev00

	As per agreed modification, platform crane has been relocated between node 4 and 5 on the platform and this led to a new supporting structure due to increased SWL of the crane.
Due to this, only for a limited area, as shown in the below snap, there is not sufficient space to keep the primary escape route, as initially foreseen with a width of 1200mm, but it will be reduced to 800mm.
It is requested to Client to accept this width reduction, as shown with the red arrows, that will lead operators with a secondary escape route, so allowing in any case an alternative escape route. The area will be properly signed with safety signs and black/yellow painting, and considering:
· The limited number of operators (max POB 10);
· The location at below deck, where fire and explosion hazards are very unlikely
· The limited expected time passed by operators at the platform (16h per year)
It is assumed that this deviation is not impacting the overall risk of the facility
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	2. Response

	Reference documents / Aconex unique numbers


	CrossWind has no objections.



This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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