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	Originating Party
	Rosetti Marino

	Subject
	Cable Ties Cushion Sleeves Material

	Author
	Rosetti Marino – Electrical Department
	TQ Aconex unique number: 123A90-PML-PM-DR-00004

	Interface TQ - from
	
	TQ interface source Aconex unique number:  

	Type
	Query
	
	Interface
	

	
	Deviation
	X
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	X
	Procurement
	X
	Construction
	X

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	14-mar-24
	Urgent reply 5 days
	X
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
· K559-2254-EL-PHI-002 Electrical System Description & Design Philosophy
· Attachment 1 Cushion Sleeve

	As per “K559-2254-EL-PHI-002 Electrical System Description & Design Philosophy” all materials used shall be halogen free and low smoke / flame retardant.

Due to the long delivery times of LSZH cushion sleeves in TPE (thermolastic elastomer), contractor proposes the supply and installation of Neoprene sleeving both for indoor and outdoor areas according to the following considerations:
· Specifications on both products are almost identical, with the exception of size and plastic material used;
· TPE is LSZH while Neoprene is Fire Resistant;
· Both Neoprene and TPE are suitable for indoor and outdoor areas;
· Neoprene withstands higher maximum Operating temperatures and lower minimum Operating temperatures, with respect to TPE;
· Neoprene withstands higher maximum Installation temperatures and lower minimum Installation temperatures, with respect to TPE;

Please refer to Attachment 1 (doc. Cushion Sleeve) for further details. 

Based on the above considerations, Contractor requests Company to acknowledge the use of Neoprene Cushion Sleeves for cable ties.


	2. Response

	Reference documents / Aconex unique numbers
	ROSMA-INN-BPH-DEV-00009 
	00 
	123A90-PML-PM-DR-00004 - Cable Ties Cushion Sleeves Material 




	Company acknowledges the use of Neoprene sleeving.



This communication is issued for the recipient’s information and to facilitate the obligations of the Parties under the Contract. This communication has no authority to amend or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.						Page 1/2
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Cushion Sleeve.pdf
Pan-Steel ® Super-Heavy
Cable Tie System

Pan-Steel® Super-Heavy Cable Tie System provides a superior
bundling solution in applications requiring cables to be safely

restrained in the event of a short circuit. Designed to work together,
Pan-Steel® Super-Heavy Cable Ties, cushion sleeve and tool provide
an 80% time savings when compared to conventional cable cleat
installations. The patented locking head design, allows these ties to
meet the critical strength requirements to restrain cables in the event

of a short circuit, with substantial reduction in material costs compared
to the conventional methods. The installation tools feature an adjustable
tension control mechanism to provide repeatable installations with consistent
bundle tension for improved productivity and reliability. The cushion sleeve
provides additional bundle protection against abrasion during and after installation.
The Pan-Steel® Super-Heavy Cable Tie System is part of the complete bundling

solution from Panduit, delivering maximum reliability throughout the physical infrastructure.

Key Features Benefits

Self-locking cable tie design Helps to reduce the number of installation steps required to deliver an 80%

installation time savings — lowering installed costs

Provides infinite bundling capacity to accommodate multiple bundle sizes to

reduce inventory and increase jobsite flexibility

Stainless steel head construction High strength construction improves durability

Reduces material required for the job (compared to competition) to deliver

a substantial cost reduction in material

Fully assembled discrete lengths Eliminates tie assembly, reducing installation time

Stainless steel construction

Superior corrosion resistance to deliver a long service life

Cushion sleeve Covers the edge of the tie to provide additional bundle and cable
jacket protection
Tension control tool Provides consistent/repeatable installations for increased reliability

and productivity

Technical Information — Super-Heavy Locking Ties

Material AISI 304 or AISI 316 RoHS Compliant
grade stainless steel

Maximum 538°C Flammability Non-flammable

temperature rating | (1000°F)

Minimum -80°CO Ultraviolet light Excellent

temperature rating | (112°F) resistance

www.panduit.com





Pan-Steel ® Super-Heavy Cable Tie System

Super-Heavy Metal Locking Ties

Max. Bundle Min. Loop Min. Bundle Std. Std.
Diameter Length*** Tensile Strength** Diameter Width Thickness Pkg. Cin.

Part Number In. mm In. mm Lbs. N In. mm In. mm In. mm Qty.+ Qty.
AISI 304 Stainless Steel — For General Purpose
MLT4SH-LP 4.0 102 17.1 434 50 250
MLT6SH-LP 6.0 152 23.4 594 50 250
MLT8SH-LP 8.0 203 29.7 754 900 4005 1.00 = 254 63 159 | 015 | .38 50 250
MLT10SH-LP 10.0 254 35.9 912 50 250
MLT12SH-Q 12.0 305 42.2 1072 25 125
AISI 316 Stainless Steel — For Superior Corrosion Resistance
MLT4SH-LP316 4.0 102 17.1 434 50 250
MLT6SH-LP316 6.0 152 23.4 594 900 4005 1.00 = 254 63 159 | 015 | .38 50 250
MLT8SH-LP316 8.0 203 29.7 754 50 250
AISI 304 Stainless Steel - Double Wrapped” - For Additional Strength
MLT4DSH-Q 4.0 102 29.5 749 25 125
MLT6DSH-Q 6.0 152 415 1054 1200 5340 1.00 = 254 63 159 | .015 | .38 25 125
MLT8DSH-Q 8.0 203 53.5 1359 25 125
AISI 316 Stainless Steel - Double Wrapped” - For Additional Strength
MLT4DSH-Q316 4.0 102 29.5 749 25 125
MLT6DSH-Q316 6.0 152 415 1054 1200 5340 1.00 = 254 .63 159 | .015 | .38 25 125
MLT8DSH-Q316 8.0 203 53.5 1359 25 125

**Per SAE Standard AS23190/3 (formerly MIS).

***QOther lengths available, contact Panduit Customer Service.
ATested for short circuit applications up to 71.5 kA.

+Order in multiples of Standard Package Quantities.

PCS Cushion Sleeving

* Black neoprene sleeving used with e Isolation between dissimilar metals
Pan-Steel® Stainless Steel Ties, custom allows the ties and straps to be used
length banding, and MS strap with aluminum cable tray
Used with Width )
Part Number Pan-Steel® Ties/Strapping In. mm Ft. m Qty+
PCSSH-B-CR* MLT/EH/SH and MS Straps .91 23.1 100 30.5 1

*Meets MIL-R-6855.
+Order in multiples of Standard Package Quantities.

Installation Tools

Std.
Pkg.
Part Number Part Description Qty.
PBTMT Battery powered installation tool, for use with Pan-Steel® heavy, extra-heavy, and super-heavy, cross section 1
MLT style ties, and MLTD double wrapped style ties, 2 —12 volt lithium-ion batteries and 115 volt, 60 Hz
charger included.
RT2HT Use with extra-heavy .50" (12.7mm) and super-heavy .63" (15.9mm) cross section Pan-Steel® type MLT ties. 1
Width of tool nose 2.60" (66.0mm).
RT2HTN Narrow nose installation tool for use with extra-heavy .50" (12.7mm) and super-heavy .63" (15.9mm) cross 1
section Pan-Steel® type MLT ties. Width of tool nose 1.06" (27.0mm).
KRT2HTB Replacement cutter handle for RT2HT. 1
WORLDWIDE SUBSIDIARIES AND SALES OFFICES
PANDUIT CANADA PANDUIT EUROPE LTD.  PANDUIT SINGAPORE PTE. LTD. PANDUIT JAPAN PANDUIT LATIN AMERICA  PANDUIT AUSTRALIA PTY. LTD.
Markham, Ontario London, UK Republic of Singapore Tokyo, Japan Jalisco, Mexico Victoria, Australia
cs-cdn@panduit.com  cs-emea@panduit.com cs-ap@panduit.com cs-japan@panduit.com  cs-la@panduit.com cs-aus@panduit.com
Phone: 800.777.3300  Phone: 44.20.8601.7200  Phone: 65.6305.7575 Phone: 81.3.6863.6000  Phone: 52.33.3777.6000 Phone: 61.3.9794.9020
For a copy of Panduit product warranties, log on to www.panduit.com/warranty
For more information ©2010 Panduit Corp.

iai H ALL RIGHTS RESERVED.

® Visit us at www.panduit.com Product Bulletin Number WW-SSCB23

n “ IT Contact Customer Service by email: cs@panduit.com Replaces SA-SSCB17
or by phone: 800-777-3300 and reference SSCB23 4/2010
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