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	1. [bookmark: _Hlk14887621]Description 

	Reference documents : 
1) Naviswork Model


	· Questions n: 1, 2 and 3 to the possibility to access the monopile:













[image: A blue tower with metal structures

Description automatically generated]1) Are these buckets / sleeves presents and surveyed? 
2) is the external walkway already installed? 
If yes, see point 4.
if not, is it already designed/fabricated and ready to be installed? can we have the dim. control? Has the trial fit been performed in yard?

3) Are these portions of ladders already installed? 
if yes, can it be used to access to the monopile?
The top part result in the area of TP installation










· Question n.4 to the installability of Caissons:
It is applicable only with the external walkways already present offshore.
[image: ]Not enough clearance for offshore installation with ext. walkway in position.
Caisson support dim. to be inserted


· Questions n.5 and 6 to the Monopile’s internal structures
[image: A computer generated image of a round structure

Description automatically generated with medium confidence]5) Is the internal walkway/structure already installed? 
6) if not, are the internal support in place? Is the internal structure already fabricated? Please provide dim. control. Has the trial fit been performed in yard?





· Questions n.7 and 8 to the upper Flange
Usually, flanges are usually manufactured together and tested for fit in workshop. Therefore: 
7) has the upper flange already been fabricated?
    if yes, has the connection already been checked? Is it available?
    if not, did Van Oord make a template of the bottom flange?

[image: A blue rectangular object with red lines

Description automatically generated]

9) Is there any Primary installation AIDS system that guides the TP into position, already designed and installed on Monopile offshore?  EXT or Internal (typ)










	2. Response

	Reference documents / Aconex unique numbers


	Q1: Yes, all buckets are present. 
Q2: Yes, the external platform is already installed (Main Access Platform) onto the Monopile (MP). 
Q3: Yes, the ladder is already installed. Note: Prior to Transition Piece (TP) installation the top section of the ladder needs to be removed (bolted section – see image below). After removal, a temporary SRL (self-retracting lanyard) support is required. Final SRL support will be from the Transition Piece girder.

[image: ]


Q4: Caisson Support frame:
The model shows a flanged connection on the support; this needs to be detailed further or alternative designs studied. 
We do see options to improve the configuration and maybe not use the upper support for the caisson frame.


Q5. Yes, this is correct. Please refer to the K559-2254-EM-GAS-005 set of drawings that define the interface between the Monopile and the Transition Piece. Some of the elements will be fabricated and installed by Rosetti, as per the interface drawing.
Q6: See above 

Q7: Section of the flange attached to MP is installed. Flange for TP is NOT fabricated. No such template is available from Van Oord. The connection between MP and TP is to be designed by Rosetti.


Q9: No guide system is installed. BLPH specific guides are to be designed and installed by Rosetti. For information, for WTG tower positioning guides are on the tower sections.



This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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