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	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers: K559-2254-EL-LAY-002 sh. 001 & 002 Rev. 1
66Kv/6.6kV Switchroom Layout & 400V Switchroom Layout

	We have found that all CPI containers are without Air locks. Similary we are forecasting our Switchroom without Air lock, please confirm.
List of our Switchroom/Equipment room:
· 66Kv/6.6kV Switchroom
· 400V Switchroom
· AC UPS Equipment room
· I&T Equipment room


	2. Response

	Reference documents / Aconex unique numbers
SRN 04272 - SAFOP Report (Define phase) -Rev A01

	BLPH SAFOP workshop reviewed the Switchroom layouts K559-2254-EL-LAY-002 sh. 001 & 002 and the need for Air-locks for the 66/6.6kV switchroom and 400V switchroom. 

Outcome/recommendations from the SAFOP workshop :
1. Air-locks should not be required as the Switchrooms are placed in non-hazardous area on the platform,
2. HVAC systems design to maximise the use of internal recirculation. HVAC with marine type filters to prevent salt laiden air from entering switchrooms.

Similar can be considered for the Equipment rooms. However, Contractor shall ensure that the equipment rooms environment is controlled adequately. 



This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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