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	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
Basic Design Engineering Package, doc. N. K559-2254-PM-PLN-003, sect. 9.7.2.3 Interfacing
Control Systems Philosophy, doc. N. K559-2254-IC-PHI-001, sect. 6.3.1 UCP Controlled

	Above referenced FEED requirement states: «The Electrolyser, the BESS and the Fuel Cell shall all be controlled via UCPs. The communication protocol between the CCS and the Electrolyser, BESS and Fuel Cell systems shall be in accordance with IEC 61158, preferably Modbus. »
Control System manufacturer ABB is suggesting to interfacing Company Provided Items with CCS employing the Profinet communication protocol instead of Modbus. Despite CCS can provide Modbus interfacing, Profinet is proposed by ABB as preferrable in terms of set-up and troubleshooting.
Company is kindly required to assess and confirm if Profinet communication protocol can be provided by STATRON for interfacing the BESS UCP.

	2. Response

	Reference documents / Aconex unique numbers


	The BESS system uses Profinet communication 
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