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	Originating Party
	Rosetti Marino

	Subject
	Sampling Frequency Rate for the Event Data Recording

	Author
	Rosetti Marino – Electrical Department
	TQ Aconex unique number:  
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	Type
	Query 
	
	Interface 
	

	
	Deviation
	x
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	x
	Procurement
	
	Construction
	

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	12/10/2023
	Urgent reply 5 days
	x
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:


	ABB who will provide the LV and MV switchgears for the BLPH Platform, is offering the multifunction protection relay REX640, which can do fault recording with a sampling frequency rate of 1,6 kHz (1500 samples/sec), while the DEP 33.64.10.32-Gen, February 2021, ELECTRICAL NETWORK MONITORING AND CONTROL SYSTEM FOR GLOBAL APPLICATION, in point 7 of clause 4.2.4 state that: “If a transient recorder function in specified, the analogue signals shall have a sampling frequency of at least 4,000 samples per second.”
Based on the above-mentioned difference on the sampling rate, Company is kindly requested to allow Contractor to proceed with ABB standard relay REX640 with a sampling frequency of 1,6 kHz, considering that 1500 samples/sec will provide sufficient resolution to perform satisfactory failure analysis.

	2. Response

	Reference documents / Aconex unique numbers


	Accepted – COMPANY deems 1500 samples/sec acceptable



This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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