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	Originating Party
	Rosetti Marino

	Subject
	Unarmoured electrical cables

	Author
	Rosetti Marino – Electrical Department
	TQ Aconex unique number:  ROSMA-INN-BPH-TQ-00080

	Interface TQ - from
	
	TQ interface source Aconex unique number:  

	Type
	Query
	
	Interface
	

	
	Deviation
	X
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	X
	Procurement
	X
	Construction
	X

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	14-mar-24
	Urgent reply 5 days
	X
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
DEP 33.64.10.10-Gen. _ ELECTRICAL ENGINEERING DESIGN
123A90-DDL-SAF-DL-30022 _ Hazardous Area Classification Layout - lower deck
123A90-DDL-SAF-DL-30023 _ Hazardous Area Classification Layout - upper deck

	As per “DEP 33.64.10.10-Gen. _ Electrical Engineering Design” electrical cable shall be armoured in offshore installations.
Contractor informs that armoured cables will be:
· Lighting circuits on upper deck
· power cables between UPS cabinets and battery banks (through isolator battery box)
· power cables starting from Distribution section of each UPS to various items.
· NavAid system
Contractor proposes to supply and install unarmoured cables for the BLPH project in safe areas according to the following reasons:
· lower deck, according to Safety layout 123A90-DDL-SAF-DL-30022, is considered safe area.
· upper deck, according to Safety layout 123A90-DDL-SAF-DL-30023, shows hazardous area only in limited areas (2m around H2 vessels and related valves/pipes)
· all containers (B-100/200/300/400) supplied by Contractor are considered safe area.
In addition to the above considerations, unarmoured cables allow for a reduction of weight and smaller bending radius with respect to armoured ones.
The Contractor highlights that all cables passing or arriving in a classified area will be protected in compliance with the requirements of the IEC 60079-14 and that cables external to the equipment will have flame propagation properties according to IEC 60332-1-1. 
Based on the above statements, Contractor requests Company to confirm the cable armouring philosophy. 


	2. Response

	Reference documents / Aconex unique numbers

	Based on our recent discussions and meetings, the Company acknowledges the cable armouring philosophy is consistent with those discussions.

Company has no technical issues with the Contractor’s armouring philosphy, noted that it is a deviation for the original specified works.





This communication is issued for the recipient’s information and to facilitate the obligations of the Parties under the Contract. This communication has no authority to amend or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.						Page 1/2
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