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	 Originating Party
	Rosetti Marino

	Subject
	Local Control Station (LCS)

	Author
	Rosetti Marino – Electrical Department
	TQ Aconex unique number:  ROSMA-INN-BPH-TQ-00081

	Interface TQ - from
	
	TQ interface source Aconex unique number:  

	Type
	Query
	
	Interface
	

	
	Deviation
	X
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	X
	Procurement
	X
	Construction
	X

	
	Commissioning
	X
	Operations
	X
	Other
	

	Issue date
	14-mar-2024
	Urgent reply 5 days
	X
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
K559-2254-PR-PID-001 – PIPING AND INSTRUMENTATION DIAGRAM SHEET 1 GENERAL NOTES AND SYMBOLOGY

	According to FEED P&ID the only indication related the Local Control Station (LCS) is: 
”Note 15. LOCAL START-STOP SWITCH AT THE MOTOR ARE NOT SHOWN.”
Contractor proposes the following control philosophy:
1) 2 sea water pumps will be controlled through BLPH CCS and not through the LCS;
2) All remaining pumps installed on BLPH will be provided and managed by the package’s vendor according to their standard (package in charge of the MEC discipline) and controlled by package UCP, without the use of any other LCS.
Based on the above philosophy, Contractor informs there is no need to provide the LCS for the BLPH.

Contractor kindly asks to confirm the acceptance of the above philosophy.


	2. Response

	Reference documents / Aconex unique numbers

	Based on our recent discussions and meetings, the Company acknowledges the LCS control philosophy is consistent with those discussions and the Company has no technical issues with what is proposed in the control philosphy.

NOTE : If no local switches are installed on motors and pumps, Contractors shall ensure that other provisions are in place (e.g. LOTO) to ensure complete de-energization in case of maintenance or other activities on the devices.


	3. CTR Response Rev.01

	LOTO are present on switchgear, as here below reported, pictures of supplied LOTO system by IMESA:
[image: ]

[image: ]
Based on CW response ROS ask to closed this TQ and will proceed with this acknowledged solution.




	4. Response

	Reference documents / Aconex unique numbers

	Company acknowledges LOTO will be in place for all circuit breakers feed in the motor devices and accepts the Contractors proposal





This communication is issued for the recipient’s information and to facilitate the obligations of the Parties under the Contract. This communication has no authority to amend or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.						Page 1/2
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