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	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
· Electrical System Description & Design Philosophy - K559-2254-EL-PHI-002_rev.03
· Basic Design Engineering Package - K559-2254-PM-PLN-003_rev02
· ELECTRICAL ENGINEERING DESIGN - 33.64.10.10-Gen_Feb.202

	Contractor developed the LPS design according to IEC 61892 standard, but this does not allow the protection level computation. Therefore, the LPL class II LPS system has been calculated according to IEC 62305-2 computation procedure (even if this standard is not applied to offshore structures), considering the platform as an area with risk of explosion. 
Contractor also informs the Company that the analysis of loss of economic value has not been performed, since the risk assessment for the BLPH is not applicable. 
[bookmark: _Hlk162433302]Contractor kindly asks the Company to confirm the above statements.

	2. Response

	[bookmark: _Hlk162431807]Reference documents / Aconex unique numbers


	Based on our recent discussions and meetings, the Company acknowledges the above statements on LPS design is consistent with those discussions and the Company has no technical issues with what is proposed in the Contractor’s LPS design and acknowledges acceptance for the referenced standards proposed for the LPS design works.


The statement about the loss of economic value calculation is also acknowledged.




This communication is issued for the recipient’s information and to facilitate the obligations of the Parties under the Contract. This communication has no authority to amend or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.						Page 1/1
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