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	Originating Party
	Rosetti Marino

	Subject
	Heat Tracing System

	Author
	Rosetti Marino – Electrical Department
	TQ Aconex unique number:  ROSMA-INN-BPH-TQ-00085

	Interface TQ - from
	
	TQ interface source Aconex unique number:  



	Type
	Query
	
	Interface
	

	
	Deviation
	X
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	X
	Procurement
	
	Construction
	X

	
	Commissioning
	X
	Operations
	X
	Other
	

	Issue date
	14-Mar-2024
	Urgent reply 5 days
	X
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:
K559-2254-EL-PHI-002_03 - BLPH Electrical System Description & Design Philosophy
K559-2254-EL-ELL-001 - Electrical Load List  rev 1
K559-2254-EL-SLD-001 - BLPH AC OPTION - KEY SLD rev2

	Reference is made to the following document “K559-2254-EL-PHI-002_03 - BLPH Electrical System Description & Design Philosophy” par.6.11. TRACE HEATING:
The document states that:
1. “A single trace-heating sub-circuit shall only supply one process system”.
2. “Sub-distribution boards for heat tracing shall operate at 230VAC, 1-Phase from a 400V TPN+E distribution board. Each outgoing circuit shall be protected by a suitably sized MCB and 30mA RCD to provide sensitive earth leakage protection.”
Contractor asks to deviate spec. and proposes to:
1. A single trace heating sub-circuit (self regulated cable) shall supply one process line and relative instruments.
2. Multiple lines or instruments on the same process systems shall be fed from a single 30mA RCBO at 230VAC from BoP distribution board DP-200N1. (See the below example)




Contractor kindly asks Company to confirm the above statements.


	2. Response

	Reference documents / Aconex unique numbers


	Based on our recent discussions and meetings, the Company acknowledges the proposed design changes to the Heat Tracing System. Company has no technical issues with the Contractor’s revised design proposal noting that it is a deviation for the original specified works

Electrical Design on 123A90-DDL-EL-DG-20162 shall be updated accordingly to this proposal and sent for review/comment. 




This communication is issued for the recipient’s information and to facilitate the obligations of the Parties under the Contract. This communication has no authority to amend or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.						Page 1/1
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