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	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:

K559-2254-EL-PHI-002 - BLPH Electrical System Description & Design Philosophy  rev3


	Document K559-2254-EL-PHI-002, paragraph 6.13, states that: “Lighting used for navigation aids, obstruction warning and where associated with aviation (where applicable) shall be provided / installed fully in accordance with guidance provided by the Marine TA2.”

As agreed previously during conference call on 20th March 2024, Contractor will follow Company requirement, as Navigational Aid, Obstruction Lights and Status Light with the applicable parts of Water Decree CWHKN-PMG-PJA-PLN-00005 received by CPY on 9th of February 2024.

As per Company mail dated 22nd of Marc 2024, the only requirements for NavAids and obstruction lights shall be as follows:
· RM to supply Obstruction Lights that are 4x2000 cd steady burning red.
· Obstruction lights – SAR mode not applicable and to be removed from WD (not in RM current scope).
· Marine lights need to be yellow rather than white.
· Marine lights – visibility range 5NM only required.

Company is requested to acknowledge the above request.


	2. Response

	Reference documents / Aconex unique numbers


	The above bullet points accurately detail the email of March 22nd from Company to Contractor. However, the bullet points detail the scope items which were misaligned only between the Water Decree and the original RM scope comparison exercise completed.
For clarity the complete scope of supply is per the attached excel spreadsheet:
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								WATER DECREE		DEP 33.80.00.30-Gen		IALA G1162
valid for marine lights on platforms		CAP437/168
valid for marine lights on platforms		ROSETTI		REMARKS		CW Comment

																				BKI comments

				AERONAUTICAL OBSTRUCTION LIGHTS		References		CAP764		CAP437		N/A		-		Comply with DEP 33.80.00.30-Gen		CAP764 applies just to wind farms

						Q.ty		2		ref to CAP437/ national requirements		N/A		4 
(platform is nore than 45mt)		Comply with CAP437/168		CW to define if to deviate from CAP standard		4x2000 cd steady burning red

						Light colour and pattern		steady burning red 		ref to CAP437/ national requirements		N/A		steady red medium and low intensity		Comply with CAP437/168				ok

						Light intensity		2000 cd		not specified		N/A		2000 cd / 200 cd (table 6A.1)		Comply with CAP437/168				ok

						Service		Switched on only during SAR operations		Switched on as function of lighting and visibility level		N/A		Switched on as function of lighting and visibility level		Comply with CAP437/168		CW to define if to deviate from CAP standard		SAR mode not applicable. Lights always on also during day (CW will propose deviation to authorities)

				MARINE LIGHTS		References		IALA O-139		IALA O-139		-		N/A		IALA G1162		IALA O-139 has been updated with IALA G1162		OK

						Q.ty		2		ref to IALAG O-139 / national requirements		≥ 2		N/A		Comply with IALAG1162				OK

						Light colour and pattern		Yellow flashing		ref to IALAG O-139 / national requirements		White flashing		N/A		Comply with IALAG1162		CW to define if to deviate from IALA standard		Yellow light

						Visibility range		≥ 5NM		ref to IALAG O-139 / national requirements		≥ 10 NM		N/A		Comply with IALAG1162				5 NM 

						Light intensity		not specified		not specified		not specified		N/A		1400 cd				ok

						Service		Switched on during night and when visibility < 2NM		Switched on during night and when visibility < 2NM		Night		N/A		Comply with DEP 33.80.00.30-Gen				ok

				FOG HORN		References		IALA O-139		IALA O-139		-		N/A		IALA G1162		IALA O-139 has been updated with IALA G1162

						Q.ty		Not required		ref to IALAG O-139 / national requirements		≥ 2		N/A		Comply with IALA G1162		CW to define if to deviate from IALA standard		Not required

						Sound pattern		Mo "U" 30s / short blast of 0,75 s		ref to IALAG O-139 / national requirements		Mo "U" 30s / short blast of 0,75 s		N/A		Comply with IALA G1162				NA

						Sound range		≥ 2 NM		ref to IALAG O-139 / national requirements		≥ 2 NM		N/A		Comply with IALA G1162				NA

						Service		When visibility < 2NM		ref to IALAG O-139 / national requirements		When visibility < 2NM		N/A		Comply with IALA G1162				Na

				STATUS LIGHT		References		N/A		CAP437		N/A		-		Comply with DEP 33.80.00.30-Gen

						Q.ty		Not required		ref to CAP437/ national requirements		N/A		1		Comply with CAP437/168		RM considers to install the status light even if helideck is not present. The lantern will be placed on the boat landing area to show if H2 is present on platform. 
CW to define if to deviate from CAP standard		OK to implement not relvant for Water Decree plan

						Light colour and pattern		N/A		ref to CAP437/ national requirements		N/A		Red Flashing		Comply with CAP437/168

						Visibility range		N/A		ref to CAP437/ national requirements		N/A		not required		Comply with CAP437/168

						Light intensity		N/A		ref to CAP437/ national requirements		N/A		700 cd or 176 cd		Comply with CAP437/168

						Service		N/A		ref to CAP437/ national requirements		N/A		Emergency/Dangerous conditions onboard the platform		Comply with CAP437/168

				ID SIGN BOARDS		References		IALA O-139/IALA 1081		not specified		-		N/A		IALA G1162

						Q.ty		3		not specified		not specified		N/A		TBD		RM asks to clarify wether ID sign boards are required by CW since not defined in Contract		ID board is already present

						Type		Black letters on yellow background 		not specified		Black letters on yellow background 		N/A		Comply with IALA G1162				Retreflective black letter yellow background. Already placed 

						Lighting		active		not specified		active or retro-reflecting				Retro-reflecting				RM to provide light to iluminate the boards

				AIS and SCADA integration		General		Required		Not mandatory		Not mandatory		N/A		Not considered		Synchronization between BLPH and Wind Farm is not forseen by RM since not defined in Contract		Deviation will be requested on the Water decree.
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