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	Originating Party
	Rosetti Marino

	Subject
	Hart revision 7 protocol 

	Author
	M. Dossena
	TQ Aconex unique number:  

	Interface TQ - from
	
	TQ interface source Aconex unique number:  



	Type
	Query
	
	Interface
	

	
	Deviation
	x
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	x
	Procurement
	
	Construction
	

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	02.05.2024
	Urgent reply 5 days
	
	Routine reply 10 days
	x

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers:

Basic Design Engineering Package, doc no. K559-2254-PM-PLN-003 rev.02


	The following requirement is specified in the referenced document “Basic Design Engineering Package”, doc no. K559-2254-PM-PLN-003 rev.02, sect. 9.7.3:
“All SIS and FGS elements shall communicate as direct point-to-point control using the 4-20mA Smart HART revision 7 protocol.”
Rosetti confirms that all F&G elements shall communicate as direct point-to-point control using the 4-20mA Smart HART revision 7 protocol.
Instead, evaluating the technical offers for electronic transmitters, we see that one vendor can only provide HART protocol revision 6 instead of revision 7 (as required by the above contractual FEED documentation).
The main outstanding difference between Hart protocol rev 6 and rev 7 is the Time Stamp (not foreseen in rev 6, mandatory in rev 7).
In any case, in the Safety System, the CPU calculates the alarm thresholds and sets the associates alarms times regardless of the hart 6 or 7 protocol of the transmitters, and these alarms times are used for the time stamping.

Company is kindly required to acknowledge the deviation is accepted.




	2. Response

	Reference documents / Aconex unique numbers


	This solution is acceptable based on the information provided by Contractor in the Description above.



This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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