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Hollandse Kust Noord
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	Rev:
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	No. TQ :
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	Originating Party
	Rosetti Marino

	Subject
	Request for information on Company Provided Item for QRA integration

	Author
	C. Caracciolo
	TQ Aconex unique number: ROSMA-INN-BPH-TQ-00099

	Interface TQ - from
	
	TQ interface source Aconex unique number:  



	Type
	Query
	X
	Interface
	

	
	Deviation
	
	Derogation (SHALL[PS])
	

	
	Note: No deviations nor derogations which have an adverse effect on HSSE will be granted

	Workpackage
	

	Area(s) of application
	Design & Eng.
	X
	Procurement
	
	Construction
	

	
	Commissioning
	
	Operations
	
	Other
	

	Issue date
	25/09/2024
	Urgent reply 5 days
	X
	Routine reply 10 days
	

	Close-out date
	
	

	Closed-out by
	
	TQ status:
	Closed-out


	1. [bookmark: _Hlk14887621]Description 

	Reference documents / Aconex unique numbers: 
123A90-DDL-SAF-RE-30019

	
In order to integrate in the QRA report CPI impacts on possible loss of life, RM propose the following assumptions when operators are accessing the platform:
1. Fuel Cell package is in process SD so no risk for operators is created
2. Electrolyser package is in process SD and depressurized so no risk for operators is created
3. BESS thermal run away is still a credible scenario.
We request Client to confirm above assumption and to provide the damage distances for the 3rd case for explosion scenarios at the thresholds of 0.5 bar (100% lethality) and 0.3 bar (50 % of lethality).


	2. Response

	Reference documents / Aconex unique numbers
123A90-DDL-SAF-RE-30019

	Assumption 1 and 2 correct for the QRA. 
 
For the BESS TR
	Volume of vapour cloud in container
	7.5 m3

	Overpressure (mbar)
	Distance (m)

	500
	3.5

	300
	6.1


 
 






This communication is issued for the recipient’s information and to facilitate the obligations
of the Parties under the Contract. This communication has no authority to amend                                                                      Page 2/2
or vary the Contract nor relieve either Party of any duties, obligations or responsibilities.								
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